## CPC Appendix A Calculation
WATER SERVICE CALCULATIONS
FIXTURE | NO. | FIX. UNIT. | TOTAL COLD | TOTAL HOT
WATER CLOSET FV (1.28GPF) | 0 | - | 0 | -
URINAL (0.5 GPF) | 0 | - | 0 | -
HOSE BIBB | 0 | 2.5 | 0 | -
HOSE BIBB (ADDITIONAL) | 0 | 1 | 0 | -
LAWN SPRINKLERS | 0 | 1 | 0 | -
WASHFOUNTAIN(CIRCULAR SPRAY)(20GPM) | 0 | 4 | 0 | 0
TUB/SHOWER | 0 | 4 | 0 | 0
SHOWER, PER HEAD (2.0GPM) | 0 | 2 | 0 | 0
CLOTHES WASHER | 0 | 4 | 0 | 0
SERVICE SINK OR MOP BASIN (2.2GPM) | 0 | 3 | 0 | 0
CLINC FAUCET | 0 | 3 | 0 | 0
WATER CLOSET GT (1.28GPF) | 0 | 2.5 | 0 | 0
DENTAL UNIT, CUSPIDOR | 0 | 1 | 0 | 0
DISHWASHER, DOMESTIC | 0 | 1.5 | 0 | 0
WASHUP SINK, EACH SET OF FAUCETS | 0 | 2 | 0 | 0
BAR SINK (1.5GPM) | 0 | 2 | 0 | 0
KITCHEN SINK (1.8GPM) | 0 | 1.5 | 0 | 0
LAUNDRY (2.2GPM) | 0 | 1.5 | 0 | 0
LAVATORY (.20GPM PER CYCLE) | 0 | 1 | 0 | 0
DRINKING FOUNTAIN OR WATERCOOLER | 0 | 0.5 | 0 | 0
TOTAL FIXTURE UNITS |  |  | 0 | 0
FLOW IN GPM
TOTAL GPM CPC CHARTS A 103.1(1) & 103.1(2) |  |  | 0 | -
EMERGENCY EYE-SHOWER STATION | 0 | 23 | 0 | -
EMERGENCY EYE-FACE STATION | 0 | 3 | 0 | -
PRE-RINSE CIRCULAR SPRAYER | 0 | 2 | 0 | -
DISHWASHER, COMMERCIAL | 0 | 0.7 | 0 | -
LAUNDRY, COMMERCIAL | 0 | 16 | 0 | -
OTHER DEMANDS |  |  | 0 | -
TOTAL FLOW IN SYSTEM |  |  | 0
MAIN LINE SIZE |  |  |  | 1.5
WATER METER SIZE |  |  |  | 1
TOTAL ENVELOPED LENGTH |  |  |  | 150
PRESSURE LOSS IN PSI
TOTAL RISE FOR HEAD LOSS |  | 0.43 X | 20 | 8.6
REQUIRED RESIDUAL PRESSURE |  |  |  | 8
PSI FLOW LOSS THROUGH WATER METER |  |  |  | 20
PSI FLOW LOSS THROUGH BACKFLOW PREVENTOR |  |  |  | 12
ADDITIONAL PRESSURE LOSSES, YARD PIPEING, ETC. |  |  |  | 0
TOTAL PRESSURE LOSS IN SYSTEM |  |  |  | 48.6
MINIMUM PSI AVAILABLE (PLUMBER TO VERIFY) |  |  |  | 60
REMAINING PSI AVAILABLE (IF NEGITIVE USE BOOSTER PUMP) |  |  |  | 11.4
PSI DROP PER 100'-0" AVAILABLE |  |  |  | 7.6
CALIFORNIA PLUMBING CODE SECTION 610.12
DOMSTIC COLD WATER MAX. (8) FOOT PER SECOND
DOMSTIC HOT WATER MAX. (5) FOOT PER SECOND
authored by Todd Miller
The availible site pressure shall be a flow tested dynamic pressure - NOT STATIC PRESSURE. This calculation shall not be valid for combination domestic water and fire sprinkler systems. By using this calculator you agree use it at your own risk. DO NOT PRINT WITHOUT PERMISSION.
DO NOT DELETE
[5 empty] | # OF TOILETS | F.U. | # OF URINALS | F.U. | COUNTER
[5 empty] | 1 | 40 | 1 | 20 | 0
[5 empty] | 2 | 70 | 2 | 35 | 1
[5 empty] | 3 | 90 | 3 | 45 | 2
[5 empty] | 4 | 105 | 4 | 53 | 3
[5 empty] | 5 | 115 | 5 | 58 | 4
[5 empty] | 6 | 125 | 6 | 63 | 5
[5 empty] | 7 | 135 | 7 | 68 | 6
[5 empty] | 8 | 145 | 8 | 73 | 7
[5 empty] | 9 | 155 | 9 | 78 | 8
[5 empty] | 10 | 165 | 10 | 83 | 9
[5 empty] | 11 | 175 | 11 | 93 | 10
[5 empty] | 12 | 185 | 12 | 98 | 11
[5 empty] | 13 | 195 | 13 | 103 | 12
[5 empty] | 14 | 205 | 14 | 108 | 13
[5 empty] | 15 | 215 | 15 | 113 | 14
[5 empty] | 16 | 225 | 16 | 118 | 15
[5 empty] | 17 | 235 | 17 | 123 | 16
[5 empty] | 18 | 245 | 18 | 128 | 17
[5 empty] | 19 | 255 | 19 | 133 | 18
[5 empty] | 20 | 265 | 20 | 138 | 19
[5 empty] | 21 | 275 | 21 | 143 | 20
[5 empty] | 22 | 285 | 22 | 148 | 21
[5 empty] | 23 | 295 | 23 | 153 | 22
[5 empty] | 24 | 305 | 24 | 158 | 23
[5 empty] | 25 | 315 | 25 | 163 | 24
[5 empty] | 26 | 325 | 26 | 168 | 25
[5 empty] | 27 | 335 | 27 | 173 | 26
[5 empty] | 28 | 345 | 28 | 178 | 27
[5 empty] | 29 | 355 | 29 | 183 | 28
[5 empty] | 30 | 365 | 30 | 188 | 29
[5 empty] | 31 | 375 | 31 | 193 | 30
[5 empty] | 32 | 385 | 32 | 198 | 31
[5 empty] | 33 | 395 | 33 | 203 | 32
[5 empty] | 34 | 405 | 34 | 208 | 33
[5 empty] | 35 | 415 | 35 | 213 | 34
[5 empty] | 36 | 425 | 36 | 218 | 35
[5 empty] | 37 | 435 | 37 | 223 | 36
[5 empty] | 38 | 445 | 38 | 228 | 37
[5 empty] | 39 | 455 | 39 | 233 | 38
[5 empty] | 40 | 465 | 40 | 238 | 39
[5 empty] | 41 | 475 | 41 | 243 | 40
[5 empty] | 42 | 485 | 42 | 248 | 41
[5 empty] | 43 | 495 | 43 | 253 | 42
[5 empty] | 44 | 505 | 44 | 258 | 43
[5 empty] | 45 | 515 | 45 | 263 | 44
[5 empty] | 46 | 525 | 46 | 268 | 45
[5 empty] | 47 | 535 | 47 | 273 | 46
[5 empty] | 48 | 545 | 48 | 278 | 47
[5 empty] | 49 | 555 | 49 | 283 | 48
[5 empty] | 50 | 565 | 50 | 288 | 49
[5 empty] | 51 | 575 | 51 | 293 | 50
[5 empty] | 52 | 585 | 52 | 298 | 51
[5 empty] | 53 | 595 | 53 | 303 | 52
[5 empty] | 54 | 605 | 54 | 308 | 53
[5 empty] | 55 | 615 | 55 | 313 | 54
[5 empty] | 56 | 625 | 56 | 318 | 55
[5 empty] | 57 | 635 | 57 | 323 | 56
[5 empty] | 58 | 645 | 58 | 328 | 57
[5 empty] | 59 | 655 | 59 | 333 | 58
[5 empty] | 60 | 665 | 60 | 338 | 59
[5 empty] | 61 | 675 | 61 | 343 | 60
[5 empty] | 62 | 685 | 62 | 348 | 61
[5 empty] | 63 | 695 | 63 | 353 | 62
[5 empty] | 64 | 705 | 64 | 358 | 63
[5 empty] | 65 | 715 | 65 | 363 | 64
[5 empty] | 66 | 725 | 66 | 368 | 65
[5 empty] | 67 | 735 | 67 | 373 | 66
[5 empty] | 68 | 745 | 68 | 378 | 67
[5 empty] | 69 | 755 | 69 | 383 | 68
[5 empty] | 70 | 765 | 70 | 388 | 69
[5 empty] | 71 | 775 | 71 | 393 | 70
[5 empty] | 72 | 785 | 72 | 398 | 71
[5 empty] | 73 | 795 | 73 | 403 | 72
[5 empty] | 74 | 805 | 74 | 408 | 73
[5 empty] | 75 | 815 | 75 | 413 | 74
[5 empty] | 76 | 825 | 76 | 418 | 75
[5 empty] | 77 | 835 | 77 | 423 | 76
[5 empty] | 78 | 845 | 78 | 428 | 77
[5 empty] | 79 | 855 | 79 | 433 | 78
[5 empty] | 80 | 865 | 80 | 438 | 79
[5 empty] | 81 | 875 | 81 | 443 | 80
[5 empty] | 82 | 885 | 82 | 448 | 81
[5 empty] | 83 | 895 | 83 | 453 | 82
[5 empty] | 84 | 905 | 84 | 458 | 83
[5 empty] | 85 | 915 | 85 | 463 | 84
[5 empty] | 86 | 925 | 86 | 468 | 85
[5 empty] | 87 | 935 | 87 | 473 | 86
[5 empty] | 88 | 945 | 88 | 478 | 87
[5 empty] | 89 | 955 | 89 | 483 | 88
[5 empty] | 90 | 965 | 90 | 488 | 89
[5 empty] | 91 | 975 | 91 | 493 | 90
[5 empty] | 92 | 985 | 92 | 498 | 91
[5 empty] | 93 | 995 | 93 | 503 | 92
[5 empty] | 94 | 1005 | 94 | 508 | 93
[5 empty] | 95 | 1015 | 95 | 513 | 94
[5 empty] | 96 | 1025 | 96 | 518 | 95
[5 empty] | 97 | 1035 | 97 | 523 | 96
[5 empty] | 98 | 1045 | 98 | 528 | 97
[5 empty] | 99 | 1055 | 99 | 533 | 98
[5 empty] | 100 | 1065 | 100 | 538 | 99
[5 empty] | 101 | 1075 | 101 | 543 | 100
[5 empty] | 102 | 1085 | 102 | 548 | 101
[5 empty] | 103 | 1095 | 103 | 553 | 102
[5 empty] | 104 | 1105 | 104 | 558 | 103
[5 empty] | 105 | 1115 | 105 | 563 | 104
[5 empty] | 106 | 1125 | 106 | 568 | 105
[5 empty] | 107 | 1135 | 107 | 573 | 106
[5 empty] | 108 | 1145 | 108 | 578 | 107
[5 empty] | 109 | 1155 | 109 | 583 | 108
[5 empty] | 110 | 1165 | 110 | 588 | 109
[5 empty] | 111 | 1175 | 111 | 593 | 110
[5 empty] | 112 | 1185 | 112 | 598 | 111
[5 empty] | 113 | 1195 | 113 | 603 | 112
[5 empty] | 114 | 1205 | 114 | 608 | 113
[5 empty] | 115 | 1215 | 115 | 613 | 114
[5 empty] | 116 | 1225 | 116 | 618 | 115
[5 empty] | 117 | 1235 | 117 | 623 | 116
[5 empty] | 118 | 1245 | 118 | 628 | 117
[5 empty] | 119 | 1255 | 119 | 633 | 118
[5 empty] | 120 | 1265 | 120 | 638 | 119
[5 empty] | 121 | 1275 | 121 | 643 | 120
[5 empty] | 122 | 1285 | 122 | 648 | 121
[5 empty] | 123 | 1295 | 123 | 653 | 122
[5 empty] | 124 | 1305 | 124 | 658 | 123
[5 empty] | 125 | 1315 | 125 | 663 | 124
[5 empty] | 126 | 1325 | 126 | 668 | 125
[5 empty] | 127 | 1335 | 127 | 673 | 126
[5 empty] | 128 | 1345 | 128 | 678 | 127
[5 empty] | 129 | 1355 | 129 | 683 | 128
[5 empty] | 130 | 1365 | 130 | 688 | 129
[5 empty] | 131 | 1375 | 131 | 693 | 130
[5 empty] | 132 | 1385 | 132 | 698 | 131
[5 empty] | 133 | 1395 | 133 | 703 | 132
[5 empty] | 134 | 1405 | 134 | 708 | 133
[5 empty] | 135 | 1415 | 135 | 713 | 134
[5 empty] | 136 | 1425 | 136 | 718 | 135
[5 empty] | 137 | 1435 | 137 | 723 | 136
[5 empty] | 138 | 1445 | 138 | 728 | 137
[5 empty] | 139 | 1455 | 139 | 733 | 138
[5 empty] | 140 | 1465 | 140 | 738 | 139
[5 empty] | 141 | 1475 | 141 | 743 | 140
[5 empty] | 142 | 1485 | 142 | 748 | 141
[5 empty] | 143 | 1495 | 143 | 753 | 142
[5 empty] | 144 | 1505 | 144 | 758 | 143
[5 empty] | 145 | 1515 | 145 | 763 | 144
[5 empty] | 146 | 1525 | 146 | 768 | 145
[5 empty] | 147 | 1535 | 147 | 773 | 146
[5 empty] | 148 | 1545 | 148 | 778 | 147
[5 empty] | 149 | 1555 | 149 | 783 | 148
[5 empty] | 150 | 1565 | 150 | 788 | 149
[5 empty] | 151 | 1575 | 151 | 793 | 150
[5 empty] | 152 | 1585 | 152 | 798 | 151
[5 empty] | 153 | 1595 | 153 | 803 | 152
[5 empty] | 154 | 1605 | 154 | 808 | 153
[5 empty] | 155 | 1615 | 155 | 813 | 154
[5 empty] | 156 | 1625 | 156 | 818 | 155
[5 empty] | 157 | 1635 | 157 | 823 | 156
[5 empty] | 158 | 1645 | 158 | 828 | 157
[5 empty] | 159 | 1655 | 159 | 833 | 158
[5 empty] | 160 | 1665 | 160 | 838 | 159
[5 empty] | 161 | 1675 | 161 | 843 | 160
[5 empty] | 162 | 1685 | 162 | 848 | 161
[5 empty] | 163 | 1695 | 163 | 853 | 162
[5 empty] | 164 | 1705 | 164 | 858 | 163
[5 empty] | 165 | 1715 | 165 | 863 | 164
[5 empty] | 166 | 1725 | 166 | 868 | 165
[5 empty] | 167 | 1735 | 167 | 873 | 166
[5 empty] | 168 | 1745 | 168 | 878 | 167
[5 empty] | 169 | 1755 | 169 | 883 | 168
[5 empty] | 170 | 1765 | 170 | 888 | 169
[5 empty] | 171 | 1775 | 171 | 893 | 170
[5 empty] | 172 | 1785 | 172 | 898 | 171
[5 empty] | 173 | 1795 | 173 | 903 | 172
[5 empty] | 174 | 1805 | 174 | 908 | 173
[5 empty] | 175 | 1815 | 175 | 913 | 174
[5 empty] | 176 | 1825 | 176 | 918 | 175
[5 empty] | 177 | 1835 | 177 | 923 | 176
[5 empty] | 178 | 1845 | 178 | 928 | 177
[5 empty] | 179 | 1855 | 179 | 933 | 178
[5 empty] | 180 | 1865 | 180 | 938 | 179
[5 empty] | 181 | 1875 | 181 | 943 | 180
[5 empty] | 182 | 1885 | 182 | 948 | 181
[5 empty] | 183 | 1895 | 183 | 953 | 182
[5 empty] | 184 | 1905 | 184 | 958 | 183
[5 empty] | 185 | 1915 | 185 | 963 | 184
[5 empty] | 186 | 1925 | 186 | 968 | 185
[5 empty] | 187 | 1935 | 187 | 973 | 186
[5 empty] | 188 | 1945 | 188 | 978 | 187
[5 empty] | 189 | 1955 | 189 | 983 | 188
[5 empty] | 190 | 1965 | 190 | 988 | 189
[5 empty] | 191 | 1975 | 191 | 993 | 190
[5 empty] | 192 | 1985 | 192 | 998 | 191
[5 empty] | 193 | 1995 | 193 | 1003 | 192
[5 empty] | 194 | 2005 | 194 | 1008 | 193
[5 empty] | 195 | 2015 | 195 | 1013 | 194
[5 empty] | 196 | 2025 | 196 | 1018 | 195
[5 empty] | 197 | 2035 | 197 | 1023 | 196
[5 empty] | 198 | 2045 | 198 | 1028 | 197
[5 empty] | 199 | 2055 | 199 | 1033 | 198
[5 empty] | 200 | 2065 | 200 | 1038 | 199
[5 empty] | 201 | 2075 | 201 | 1043 | 200

## Pipe Friction Loss
Water Pipe Friction Loss
| IPS average outer diameter | 4.8 | in
| Pipe section eveloped length | 114 | ft
| Flow | 211 | GPM
| pipe dimension ratio | 19.2
| C | 110
| di | 4.28 | in
| friction loss Pf | 1.4552 | psi
| average velovity V | 5.5865 | ft/s
Hazen-Williams Friction Factor
C=150 for HDPE & CPVC, C=140 for copper
C=120 for galv. iron & brass, C=110 for ductile iron
𝑃𝑓=(0.0009015∙𝐿)/〖𝑑𝑖〗^4.8655 ((100∙𝑄)/𝐶)^1.85